LEGION CONTROLS

# MASTER
ARCHITECTURE

Product ecosystem, system topology, controller family, programming environment, deployment model, and engineering decision register

| Document ID | LC-ARCH-001 |
| --- | --- |
| Version | 0.1 |
| Status | Baseline working architecture |
| Date | September 13, 2026 |
| Owner | Legion Controls |

Purpose

This document is the source-of-truth baseline for the Legion Controls ecosystem. It is intended to keep human contributors and AI engineering tools aligned while the platform moves from software prototypes toward field-ready commercial products.

Important: “decided” means the direction is locked at the architecture level. It does not mean every electrical, mechanical, firmware, compliance, or manufacturing detail has been completed.

# Document Control & Reading Rules

| Label | Meaning |
| --- | --- |
| DECIDED | Approved product or architecture direction. Change only through an explicit recorded decision. |
| CURRENT | Describes the present implementation. It may be replaced as the product matures. |
| PLANNED | Intended capability or product direction; detailed design is not complete. |
| OPEN QUESTION | Requires engineering, testing, commercial analysis, or a founder decision before it is locked. |

## Authority

This document governs terminology and high-level system boundaries.

The repositories govern what the software currently does.

Electrical schematics, PCB files, firmware requirements, test plans, and compliance records will become separate controlled documents.

If this document conflicts with a newer signed decision record, the newer decision wins and this document must be updated.

## How AI collaborators must use this document

Read the whole document before recommending a major architectural change.

Explain the current architecture back before proposing a redesign.

Preserve decided boundaries unless a concrete risk justifies reopening them.

Distinguish known implementation facts from assumptions.

Treat Legion Controls as a commercial BAS ecosystem that must be installable, serviceable, secure, and supportable for years.

## Revision History

| Version | Date | Summary |
| --- | --- | --- |
| 0.1 | 2026-09-13 | Initial architecture baseline and naming lock. |

# 1. Executive Architecture Summary

Legion Controls is a locally autonomous Building Automation Systems platform. Each site is designed to continue operating without cloud connectivity. Remote access is an optional secure path into the site; it is not required for local control.

DECIDED  The Legion Server (LS-100) is the on-site PC/server that hosts the operator platform and site services.

DECIDED  Sentry G1 is an edge/gateway appliance attached to the site Ethernet network. It is not an inline device between the LS-100 and the Ethernet switch.

DECIDED  The programmable controller family uses LPC names. The first general controller is LPC0810: Legion Programmable Controller with 8 inputs and 10 outputs.

DECIDED  VAV controllers use the LPCV family prefix followed by their I/O designation.

DECIDED  The engineering and programming tool is Legion Commander Programming Environment (LCPE).

PLANNED  Legion Web provides the operator experience: navigation, graphics, points, alarms, schedules, trends, histories, and equipment management.

## Canonical topology

| Layer | Primary product | Connection / role |
| --- | --- | --- |
| Operator & engineering | Legion Web / LCPE | Operator workflow and controller engineering |
| Site compute | LS-100 | Hosts local application, APIs, database, historian, and site integrations |
| IP network | Managed Ethernet switch | Connects LS-100, Sentry G1, IP controllers, service devices, and approved integrations |
| Edge / field gateway | Sentry G1 | Bridges or supervises field networks such as BACnet MS/TP |
| Field control | LPC0810 / LPCV family | Executes equipment control locally and exposes BACnet objects |
| Remote access | Secure tunnel / approved gateway | Optional authenticated access to site services |

# 2. Vision & Design Principles

Local-first operation: loss of Internet service must not stop equipment control or normal local BAS operation.

Distributed control: critical HVAC sequences execute in field controllers, not only in the LS-100.

Technician-first serviceability: network layout, indicators, service access, replacement, and commissioning must work at the equipment.

Clear product boundaries: operator software, site compute, gateways, controllers, and programming tools have distinct responsibilities.

Open interoperability: use BACnet correctly and document vendor-specific extensions.

Progressive scalability: the same concepts should serve small stand-alone sites and larger multi-building sites.

Secure by design: least privilege, explicit trust boundaries, auditable changes, protected credentials, and safe remote access.

Long-life maintainability: favor predictable behavior, recoverable configurations, versioned artifacts, diagnostics, and replacement workflows.

## Commercial lifecycle

| Phase | Required system support |
| --- | --- |
| Engineering | Templates, programs, point definitions, network design, graphics, naming, and validation |
| Programming | Offline and connected controller programming through LCPE |
| Installation | Clear wiring, addressing, mounting, power, network, labeling, and checkout |
| Commissioning | Discovery, point selection, calibration, overrides, functional testing, and acceptance |
| Operation | Graphics, commands, schedules, alarms, trends, reports, and status |
| Troubleshooting | Live values, communication diagnostics, service access, logs, and safe overrides |
| Service | Backup, restore, replacement, firmware management, documentation, and audit history |

# 3. Product Naming Standard

| Name | Meaning | Naming rule | Status |
| --- | --- | --- | --- |
| Legion Server | On-site BAS server/computer | Model: LS-100 | DECIDED |
| Sentry G1 | First-generation Legion edge/gateway | Keep product name; hardware revision is separate | DECIDED |
| LPC0810 | Legion Programmable Controller | LPC + two-digit input count + two-digit output count | DECIDED |
| LPCV#### | Legion programmable VAV controller | LPCV + final I/O code after VAV hardware definition | DECIDED family; suffix open |
| Legion Commander Programming Environment | Controller engineering/programming application | Acronym: LCPE | DECIDED |
| Legion Web | Operator-facing BAS application | Product name retained | CURRENT / PLANNED evolution |

## I/O code interpretation

LPC0810 means 8 physical inputs and 10 physical outputs. The code describes physical I/O count, not network ports, software points, BACnet objects, or virtual variables. I/O type mix must be defined in the controller electrical specification.

OPEN QUESTION  Confirm whether every future LPC model will use exactly four digits, how universal I/O is counted, and how expansion modules are named.

OPEN QUESTION  Select the first LPCV suffix only after the VAV controller input/output schedule is frozen. Do not invent the model number earlier.

## Reserved document terminology

“Server” means LS-100 unless a generic server is explicitly stated.

“Gateway” means Sentry G1 or another named gateway; it does not mean every IP controller.

“Controller” means an LPC-family field controller unless a third-party controller is named.

“Commander” or “LCPE” means the engineering/programming environment.

Use “BACnet/IP” for BACnet transported over IP. Use “Ethernet” or “IP network” for the underlying network. Do not label every Ethernet link as BACnet/IP.

# 4. System Topology & Network Boundaries

## Physical/logical arrangement

| From | To | Link | Purpose |
| --- | --- | --- | --- |
| LS-100 | Managed switch | Ethernet/IP | Site application traffic, database access, management, integrations |
| Sentry G1 | Managed switch | Ethernet/IP | Gateway management and BACnet/IP participation where enabled |
| Sentry G1 | MS/TP trunk | RS-485 BACnet MS/TP | Communication with MS/TP controllers and devices |
| LPC IP model | Managed switch or approved field topology | Ethernet/IP | Controller BACnet/IP, management, and engineering traffic |
| Technician device | Controller service interface or site network | Service connection | Commissioning, diagnostics, upload/download, and recovery |
| Remote user | LS-100/site access boundary | Encrypted tunnel | Optional remote operator or engineering access |

DECIDED  Sentry G1 connects as a network node. It does not sit physically inline between LS-100 and the switch.

DECIDED  For an MS/TP segment, Sentry G1 sits logically between the Ethernet/IP side and the RS-485 field bus.

DECIDED  An Ethernet cable is the physical/data-link connection. BACnet/IP is one application protocol that may use the IP network; management and service traffic may use TCP or UDP independently.

## Illustrative topology

| Site Ethernet LAN |  | Field networks |
| --- | --- | --- |
| Operator browser → LS-100 | ↔ managed switch ↔ | Sentry G1 → BACnet MS/TP trunk |
| LCPE workstation | ↔ managed switch ↔ | BACnet/IP LPC controllers |
| Approved remote tunnel | → LS-100 / controlled services | No direct uncontrolled exposure of field devices |

# 5. Legion Server — LS-100

The LS-100 is the on-site compute platform for Legion’s supervisory BAS functions. It is not the only place where control logic lives; field controllers retain responsibility for safe, continuous equipment control.

## Responsibilities

Host Legion Web and its backend services.

Maintain the site database, equipment hierarchy, users, permissions, configuration, and audit records.

Collect and serve trends/history.

Process supervisory alarms and notifications while preserving controller-local protection.

Coordinate schedules and supervisory commands.

Manage integrations and northbound APIs.

Provide backup, restore, diagnostics, and deployment services.

Support secure remote access when commissioned for the site.

## Non-responsibilities

The LS-100 must not be required for every control loop to continue running.

It is not an unmanaged bridge inserted between ordinary Ethernet devices.

It does not replace controller safety logic, equipment safeties, or code-required protection.

CURRENT  Legion’s software stack uses a React frontend and a Node.js/Express backend with Prisma and PostgreSQL as the present baseline.

PLANNED  Formalize LS-100 hardware tiers, operating system image, update strategy, watchdog behavior, storage sizing, backup media, and high-availability options.

# 6. Sentry G1 Edge Gateway

Sentry G1 provides the field-network boundary and edge services needed to connect Legion’s site platform to BACnet and other building networks. Its precise feature set must remain disciplined so it does not become an accidental duplicate of LS-100.

## Primary role

Connect to the site Ethernet LAN through the managed switch.

Interface with one or more isolated RS-485 BACnet MS/TP trunks as supported by final hardware.

Perform controlled discovery, routing/gateway functions, health monitoring, diagnostics, and data exchange.

Expose clear trunk and device status to Legion Web and LCPE.

Continue predictable operation during loss of upstream connectivity.

## Field-network behavior

Only one process owns each serial interface at a time.

Discovery, polling, health checks, and writes must be coordinated to prevent bus contention.

Queued work must be cancellable or paused when discovery requires exclusive bus access.

MS/TP timing, token handling, MAC addressing, baud rate, termination, biasing, grounding, and isolation must be validated against applicable standards and field conditions.

OPEN QUESTION  Freeze Sentry G1 production hardware: processor, storage, number of Ethernet and isolated RS-485 ports, power input, enclosure, environmental ratings, service interface, and certifications.

# 7. LPC Controller Family

## LPC0810

LPC0810 is the first named general-purpose Legion Programmable Controller. The model name indicates 8 inputs and 10 outputs. It is intended for equipment such as fan coils, air handlers, pumps, and other applications that fit its eventual I/O and performance specification.

| Area | Architecture intent | Status |
| --- | --- | --- |
| Control execution | Deterministic local execution of downloaded control applications | PLANNED |
| I/O | 8 inputs and 10 outputs; exact electrical mix TBD | NAME DECIDED / MIX OPEN |
| Communications | BACnet and dedicated engineering/service access as finalized | PLANNED |
| Retention | Program and essential configuration survive power loss | PLANNED |
| Diagnostics | Power, run, fault, network, and I/O diagnostics suitable for field service | PLANNED |
| Recovery | Documented safe firmware recovery and controller replacement process | PLANNED |

## LPCV family

LPCV identifies Legion controllers purpose-built for variable air volume boxes. The family should support VAV-specific sensing, actuator control, airflow balancing, occupancy, reheat options, and commissioning workflows. The final numeric suffix will encode the frozen physical I/O count.

OPEN QUESTION  Decide whether the first LPCV includes an integrated actuator, differential pressure sensor, and/or dedicated room sensor bus.

## Controller autonomy

Equipment sequence continues when LS-100, Sentry G1, or remote access is unavailable.

Network values use explicit fallback behavior and age/stale detection.

Persistent overrides, schedules, and command priorities follow documented rules.

Controller startup, brownout, watchdog, and failed-sensor behavior must be deterministic.

# 8. Controller Networking & Technician Service Access

Normal building communication and local technician access are separate use cases, even if they share some underlying hardware. A technician at an FCU must have a clear, documented way to connect to its LPC without disconnecting the building network.

## Normal communications

PLANNED  Ethernet-capable LPC controllers may use a field daisy chain only if the controller contains a properly designed two-port embedded Ethernet switch and the topology is validated for failure behavior, latency, scale, and service replacement.

OPEN QUESTION  The final controller network architecture—home-run/star, two-port line topology, MS/TP variant, or multiple SKUs—has not been locked.

## Dedicated service interface concept

PLANNED  Use a visually distinct USB-C physical service port so a technician can connect locally without consuming or unplugging normal Ethernet ports.

USB-C describes the connector only; it does not by itself define the protocol.

A USB-C-to-RJ45 adapter can provide an isolated/local Ethernet service link if the controller implements USB networking or USB-host support correctly.

Alternatively, USB-C can expose a direct USB device interface for LCPE commissioning and recovery.

The service path should provide local addressing/discovery, authentication, safe program transfer, live diagnostics, and recovery.

The production design must protect against incorrect cables, power-role confusion, ESD, ground differences, unauthorized access, and accidental impact on live control.

CURRENT  A Mango travel router connected through a USB-C Ethernet adapter is a useful prototype/service-access experiment, not yet a production controller interface standard.

OPEN QUESTION  Choose USB device mode versus USB-host Ethernet adapter support, define whether the port supplies/accepts power, and establish the exact LCPE discovery and authentication flow.

# 9. Legion Commander Programming Environment — LCPE

LCPE is the engineering environment for creating, editing, validating, downloading, commissioning, and troubleshooting LPC controller applications. It fills the same product role that CCT fills in the Johnson Controls ecosystem, while using Legion’s own workflows and architecture.

## Core modes

| Mode | Purpose |
| --- | --- |
| Overview | Inputs on the left, outputs on the right, and central operating state / mode summary. |
| Logic View | Graphical connected-block view of the complete control sequence. |
| Network Config | Controller identity, BACnet settings, ports, addressing, time, security, and communications. |
| Pre-Building | Select equipment/application templates that populate a default program. |
| View Code | Inspect and edit the underlying program, variables, conditions, loops, and functions. |
| Commissioning | Live values, commands, calibration, balancing, diagnostics, download, and validation. |

## Operating model

Connect to one controller at a time for direct service, or build applications offline.

Validate application compatibility against controller model, firmware, I/O resources, memory, and supported features.

Transfer a versioned application package to the controller.

Retain source, compiled/deployable artifact, parameters, checksums, versions, and change history.

Make online changes explicit and recoverable; never hide divergence between the controller and saved project.

OPEN QUESTION  Choose the controller programming language/runtime and the relationship between graphical blocks and generated/editable source code.

# 10. Legion Web Operator Platform

Legion Web is the daily operator workspace. Its design goal is to reduce tab overload and keep the most useful information close to the selected site, building, floor, or equipment.

## Navigation and modes

Hierarchy: Site → Building → Floor → Equipment.

Default workspace: Operator Dashboard / Site Layout.

Mode selector: Operator Dashboard, Commissioning, and Engineering as authorized.

Top-level visibility for last synchronization and logs.

Sidebar actions include hierarchy management controls, Action, and Settings.

## Equipment workspace

| Card | Purpose |
| --- | --- |
| Graphic | Equipment visualization and primary commands. |
| Trends | Configured point history with live continuity and explicit offline/stale intervals. |
| Points Overview | Managed points, current value/status, alarm indication, and quick operations. |
| Details | Identity, metadata, network, controller, and service information. |

Cards can expand without losing the selected equipment context.

Site, building, and floor levels use a focused single-card view where appropriate.

Alarm counts propagate upward through the hierarchy.

Occupancy control opens a schedule modal showing current state, today, and weekly template.

A point becoming stale must not make its trend disappear; the chart should represent the offline interval and last valid timestamp.

CURRENT  The UI is being simplified around reusable cards while preserving working BAS functionality.

# 11. BACnet Architecture

## Protocol separation

| Term | Correct use |
| --- | --- |
| Ethernet | Local data-link/network medium used by IP traffic. |
| IP | Network-layer addressing and routing. |
| TCP / UDP | Transport protocols used by different application services. |
| BACnet/IP | BACnet messages transported using IP networking; conventionally uses UDP. |
| BACnet MS/TP | BACnet data link using token passing over RS-485. |
| BACnet/SC | Secure BACnet transport option to evaluate for future architecture. |

## Object and device behavior

Use stable BACnet device instances, object identifiers, names, units, states, and descriptions.

Honor priority arrays, relinquish defaults, commandability, status flags, and out-of-service semantics.

Document proprietary objects or properties and minimize unnecessary vendor lock-in.

Discovery should not automatically enroll every discovered point for continuous management.

Point discovery results appear in a review interface; users select the points to manage.

Managed points and discovered points remain conceptually distinct.

OPEN QUESTION  Define BACnet device-instance allocation, BBMD/foreign-device strategy, network-number allocation, segmentation, routing limits, and certification path.

# 12. Data, Trends, Alarms & Schedules

## Point lifecycle

1.  Discover device.

2.  Add the device to management with zero managed points initially.

3.  Run point discovery and retain the latest discovery results.

4.  Select the points to manage.

5.  Begin polling/subscription, status evaluation, alarming, and trending only as configured.

## Quality and stale behavior

Every displayed value needs timestamp and quality/status metadata.

Stale thresholds reflect expected update rate and communication type.

A stale point remains visible with its last valid value, last valid time, and stale/offline status.

Trends preserve the time axis and display gaps or offline bands rather than disappearing.

Recovery from stale state is recorded and does not fabricate historical samples.

## Trends

No enabled trend: show a configuration message and action.

Configured with no history: show available live value at “now” and a waiting-for-history state.

History available: show the selected point’s actual historian series.

Live anchors are not silently persisted or backfilled as historical samples.

## Alarms and schedules

Alarm configuration, detection, acknowledgement, clearing, routing, and audit history are distinct states/actions.

Counts roll up from point/equipment to floor/building/site.

Schedules support current occupancy, exceptions, today’s behavior, and reusable weekly templates.

Controller-local fallback behavior is defined for loss of supervisory scheduling communication.

# 13. Security & Remote Access

Legion sites should not require public exposure of controllers or the LS-100. Remote access is added deliberately through a secure, authenticated mechanism such as a managed tunnel, subject to customer policy.

## Trust zones

| Zone | Examples | Control intent |
| --- | --- | --- |
| User | Operator browser, LCPE workstation | Authenticated, role-scoped access |
| Site services | LS-100 applications and database | Hardened host, encrypted secrets, backups, audit logs |
| Management LAN | Switch, Sentry G1, IP controllers | Restricted access and documented addressing |
| Field bus | BACnet MS/TP devices | Physical/network controls and gateway mediation |
| Remote | Internet/cloud/tunnel service | No implicit trust; explicit identity and policy |

Unique credentials; no universal production defaults.

Role-based permissions for viewing, commanding, overriding, programming, and administration.

Signed or integrity-checked software/firmware and controlled update process.

Encrypted remote traffic and protected secrets at rest.

Security event and configuration-change audit logs.

Documented patching, vulnerability response, backup, restore, and decommissioning.

OPEN QUESTION  Select the remote-access product/architecture, device identity method, certificate lifecycle, secure boot strategy, firmware signing, and customer IT integration requirements.

# 14. Deployment, Commissioning & Service

## Site deployment flow

1.  Survey customer network, equipment, power, field buses, cybersecurity rules, and installation environment.

2.  Engineer controller applications, point lists, graphics, alarms, schedules, trends, and addressing.

3.  Stage LS-100, Sentry G1, controllers, switch configuration, backups, and credentials.

4.  Install, label, terminate, power, and inspect all hardware.

5.  Discover and enroll devices; select managed points.

6.  Download programs and parameters through LCPE; validate versions and checksums.

7.  Perform I/O checkout, calibration, balancing, sequence testing, alarm testing, failover testing, and operator acceptance.

8.  Deliver as-built documentation, backups, training, warranty, and support contacts.

## Service principles

A replacement controller can be identified, installed, addressed, restored, and verified without reverse engineering the site.

Technicians can reach local diagnostics at the equipment through an approved service workflow.

Overrides are visible, time-bounded where appropriate, and auditable.

Failure of a downstream controller in a line topology must have a documented effect and recovery method.

The site can export a support bundle without exposing unnecessary credentials or customer data.

# 15. Engineering & Product Roadmap

| Horizon | Focus | Exit evidence |
| --- | --- | --- |
| Now | Stabilize Legion Web and Sentry prototypes; lock naming and architecture boundaries | Repeatable local deployment, tests, documentation, known issues |
| Controller feasibility | LPC0810 requirements, I/O matrix, CPU/runtime, network/service concept | Approved product requirements and bench proof-of-concept |
| Engineering tool MVP | LCPE offline project, template, connect, validate, download, live values | End-to-end program lifecycle on prototype controller |
| Pilot system | Small site with LS-100, Sentry G1, LPC controllers, trends/alarms/schedules | Documented commissioning and sustained operation |
| Production readiness | DFM, enclosure, EMC/environmental testing, cybersecurity, manufacturing test | Controlled pilot build and certification plan |
| Commercial scale | Installer workflow, support tooling, spares, licensing, training, updates | Repeatable sale, install, acceptance, and support process |

## Near-term priority order

1.  Finish certification focus and maintain disciplined development scope.

2.  Stabilize core Legion Web operator behavior and deployment.

3.  Define LPC0810 product requirements before selecting final hardware.

4.  Prototype the controller-to-LCPE programming/service path.

5.  Validate real field networking, stale behavior, discovery, and recovery.

6.  Run a constrained pilot before expanding the controller family.

# 16. Decision Register

| ID | Decision | State |
| --- | --- | --- |
| D-001 | The on-site PC/server product is Legion Server, model LS-100. | DECIDED |
| D-002 | Sentry G1 is a switched LAN node and field gateway, not inline between LS-100 and the switch. | DECIDED |
| D-003 | General programmable controllers use LPC; LPC0810 means 8 inputs and 10 outputs. | DECIDED |
| D-004 | VAV controllers use the LPCV family; final suffix follows frozen I/O count. | DECIDED |
| D-005 | The programming tool is Legion Commander Programming Environment (LCPE). | DECIDED |
| D-006 | Each customer site is locally operational; remote connectivity is optional. | DECIDED |
| D-007 | Controller service access must be usable at the equipment without unplugging normal network links. | DECIDED intent |
| D-008 | USB-C is the preferred distinct physical service-port concept, pending electrical/protocol design. | PLANNED |
| D-009 | Point discovery and point management are separate workflows. | DECIDED |
| D-010 | Stale/offline points remain represented in trends; data is not fabricated. | DECIDED |

## Change rule

A proposed change must identify the affected decision, reason, field impact, compatibility impact, migration path, validation evidence, and approval. Editing terminology casually in code or UI does not change the architecture.

# 17. Open Engineering Questions

| Area | Question | Evidence required |
| --- | --- | --- |
| LPC0810 I/O | Exact mix of universal/digital/analog inputs and relay/triac/analog outputs? | Target equipment matrix, electrical design, cost |
| Controller network | Star Ethernet, two-port switched line, MS/TP SKU, or combination? | Failure testing, scale, install cost, cyber review |
| USB-C service | USB device network, serial/recovery, or host-mode Ethernet adapter? | Prototype, ESD/power tests, technician workflow |
| Runtime | Native firmware, RTOS, Linux-class platform, PLC runtime, or custom VM? | Determinism, safety, maintainability, BOM |
| Programming model | Graphical blocks, textual language, generated code, or hybrid? | Round-trip rules, debugging, IP strategy |
| BACnet | BTL listing targets and supported profiles? | Market needs and certification plan |
| Sentry hardware | Port count, isolation, storage, power, enclosure, environment? | Gateway PRD and prototype testing |
| LS-100 | Hardware tiers, lifecycle, backups, update channel, UPS strategy? | Site sizing and support model |
| Cybersecurity | Identity, certificates, secure boot, signed updates, SBOM, disclosures? | Threat model and compliance roadmap |
| Licensing | Site/controller licensing and offline entitlement behavior? | Commercial model and failure-mode policy |

## Required next controlled documents

LPC0810 Product Requirements Document (PRD)

LPC0810 preliminary I/O and electrical specification

Controller networking and service-port trade study

LCPE product requirements and application-file specification

Sentry G1 PRD and field-network specification

LS-100 deployment and lifecycle specification

BACnet object/naming/addressing standard

Cybersecurity threat model and update policy

Site commissioning and acceptance test plan

# 18. Claude / AI Project Brief

Use the following operating instruction with this document in any AI project workspace:

You are a long-term engineering partner on Legion Controls, a real commercial Building Automation Systems ecosystem. Read this entire architecture document before making major recommendations. Treat DECIDED items as binding unless you identify a concrete reliability, safety, networking, electrical, cybersecurity, manufacturability, maintainability, standards, or field-service risk. Distinguish the present implementation from planned products and open questions. Inspect the relevant repository before making software changes. Preserve working behavior and architectural continuity. Evaluate every proposal across engineering, programming, installation, commissioning, operation, troubleshooting, and service. Do not treat Legion as a generic web application, IoT hobby project, or proof of concept.

## First review prompt

Read the complete Legion Controls Master Architecture. First explain the architecture back to me using the locked product names. Then identify contradictions, missing decisions, technical risks, and questions. Do not redesign the system yet. Separate findings into: conflicts with decided architecture, implementation gaps, product risks, and open decisions. Cite the relevant section or decision ID for each finding.

## Locked names — quick reference

| Product | Locked name |
| --- | --- |
| On-site server | Legion Server — LS-100 |
| Edge gateway | Sentry G1 |
| General controller | LPC0810 |
| VAV controller family | LPCV + final I/O code |
| Programming environment | Legion Commander Programming Environment — LCPE |
| Operator application | Legion Web |