LEGION CONTROLS

# ENGINEERING &
DEPLOYMENT
ARCHITECTURE

Offline project ownership, Legion Site Package, LS-100 commissioning, activation, rollback, controller-program boundaries, and as-built synchronization

| Document | Value |
| --- | --- |
| Document ID | LC-ARCH-002 |
| Version | 1.0 |
| Status | DECIDED architecture baseline |
| Date | September 13, 2026 |
| Companion document | LC-ARCH-001 — Legion Controls Master Architecture |

Purpose

This document defines how an engineered Legion project becomes the live configuration of a customer LS-100. It replaces development seed data as the conceptual deployment mechanism and separates offline engineering data from live operational data.

# 1. Locked Product Boundaries

DECIDED  One LS-100 owns one active Legion Site in the initial commercial architecture. A Site may contain multiple buildings, floors, networks, controllers, and equipment.

DECIDED  The Legion Engineering Workspace is the offline site-level engineering environment. It creates and versions the customer project.

DECIDED  LCPE is the controller-level programming environment for LPC0810 and LPCV applications. It is not the site database builder.

DECIDED  Legion Web Operator Mode runs against the active LS-100 site and is not an offline design tool.

DECIDED  A production LS-100 is commissioned using a versioned Legion Site Package, never a development seed.

| Product/domain | Owns |
| --- | --- |
| Legion Engineering Workspace | Site hierarchy, graphics, point models, mappings, alarms, trends, schedules, network design, deployment package |
| LCPE | Controller source, logic, I/O configuration, compiled/deployable controller application, commissioning |
| LS-100 | Active site configuration, live values, historian, alarms/events, operational users, backups, deployment history |
| Sentry G1 | Field-network connectivity, routing/gateway functions, field diagnostics |
| LPC0810 / LPCV | Local deterministic equipment control and controller-resident configuration |

# 2. Authoritative Data Model

| Information | Offline project | Live LS-100 | Transfer rule |
| --- | --- | --- | --- |
| Site/building/floor/equipment | Editable master | Active deployed copy | Included |
| Graphics and bindings | Editable master | Active deployed copy | Included |
| Trend/alarm/schedule definitions | Editable master | Active definitions | Included |
| Live values and quality | None | Authoritative | Excluded |
| Trend history | None | Authoritative | Excluded |
| Alarm/event/audit history | None | Authoritative | Excluded |
| Users and credentials | Policy/roles only | Operational authority | Secrets excluded |
| Controller applications | Source + built artifacts | Deployed version record | Referenced or bundled |
| Network commissioning values | Designed values | Verified live values | Merge/validation rules |
| Backups | Project versions | Config + runtime backup | Separate artifacts |

The engineering project is authoritative for intended configuration. The LS-100 is authoritative for current live state and operational history. Deployment must never erase historian, alarm/event, audit, or credential data unless an explicit destructive restore is separately authorized.

# 3. Legion Site Package

DECIDED  The portable deployment artifact uses the extension .lspkg and the name Legion Site Package.

Example: Strip_Plaza_v1.0.0.lspkg

## Required contents

Manifest: package ID, site ID, semantic version, created time, author, tool version, minimum LS-100 version, schema version, checksums and signature.

Site hierarchy and stable logical identifiers.

Equipment definitions, templates, point definitions, resolved mappings and controller associations.

Graphics, assets and bindings.

Alarm, trend and schedule definitions.

BACnet/network configuration intended for deployment.

Controller application references and optionally compatible signed deployment artifacts.

Validation report, release notes and declared deployment scope.

## Explicit exclusions

Historical samples, alarm/event history and audit logs.

Current present values and runtime communication state.

Passwords, private keys, bearer tokens and machine secrets.

Development-only SIM records unless the package is explicitly marked for simulation.

Raw PostgreSQL database dumps or unstable environment-specific database IDs.

The package must be deterministic, integrity checked, forward/backward compatibility checked, and reject partial or tampered contents before activation.

# 4. Deployment Paths

## Direct deploy over LAN

1.  Engineer validates and builds an immutable site package.

2.  Engineering Workspace discovers or targets the LS-100 by approved address.

3.  Engineer authenticates with deployment permission.

4.  LS-100 receives the package into a staging area.

5.  LS-100 validates identity, signature, compatibility, references, mappings and deployment scope.

6.  UI presents a change preview and impact summary.

7.  LS-100 creates a pre-deployment backup.

8.  Engineer authorizes activation.

9.  LS-100 applies the configuration transactionally, runs post-activation checks and records the result.

10.  On failure, LS-100 rejects or rolls back to the previous active version.

## Offline export/import

1.  Engineering Workspace exports the same .lspkg file.

2.  File is transported using an approved removable-media or secure-transfer process.

3.  Authorized user opens Import Site Package on the LS-100.

4.  LS-100 performs the identical staging, validation, preview, backup, activation and rollback workflow.

DECIDED  Direct deployment and offline import consume the same package and validation pipeline. They must not become separate configuration formats.

# 5. LS-100 Commissioning State Machine

| State | Meaning | Allowed transition |
| --- | --- | --- |
| UNCOMMISSIONED | Legion software installed; no active Site | Import/deploy package |
| STAGED | Package uploaded but not active | Validate, discard |
| VALIDATED | Package passed validation | Preview, activate, discard |
| ACTIVATING | Transactional deployment in progress | Complete or rollback |
| ACTIVE | One Site version serves Operator Mode | Stage newer version, backup, upload |
| FAILED | Activation did not complete | Inspect, retry, rollback |
| ROLLBACK | Previous known-good version being restored | Return to ACTIVE or FAILED |

## Initial LS-100 image

Legion runtime and operator application

Empty operational database and migration baseline

Unique device identity and certificate material

Initial secure commissioning workflow

Package import/deployment service

Backup, restore, health and recovery services

Initial message: “No Legion Site commissioned. Connect using the Legion Engineering Workspace or import a Legion Site Package.”

# 6. Deployment Semantics

| Term | Locked meaning |
| --- | --- |
| Save Project | Persist edits in the offline engineering project only. |
| Validate Project | Run structural, compatibility, mapping, network and deployment checks. |
| Build Site Package | Create an immutable signed/versioned .lspkg. |
| Deploy to LS-100 | Transfer a package directly to a target LS-100 staging service. |
| Export Site Package | Save the portable package for offline transport. |
| Import Site Package | Place a package into LS-100 staging. |
| Activate | Make a validated staged version the active live configuration. |
| Upload/Retrieve | Bring current LS-100 configuration/as-built changes into an engineering project. |
| Backup | Capture recoverable LS-100 configuration and required runtime state. |
| Rollback | Reactivate the prior known-good site configuration. |

DECIDED  The current “Deploy to Live” button should evolve into Build Site Package plus Deploy to LS-100. It must not simply copy records within one database and call that a commercial deployment.

# 7. Change Preview, Activation & Rollback

## Required preview

Added, changed and removed buildings, floors, equipment, points and networks.

Mapping changes and unresolved logical points.

Graphics, alarms, trends and schedules affected.

Controller/application version changes.

Potential interruptions, restarts and devices requiring later controller download.

Objects intentionally preserved: history, events, users, credentials and audit records.

## Activation requirements

Package remains immutable after build.

Pre-deployment backup completes successfully.

Database/configuration changes occur in a transaction or equivalent staged swap.

Active version pointer changes only after validation succeeds.

Post-activation health checks run and deployment result is audited.

Failed activation automatically returns to a known-good version when safe.

## Partial deployments

The first implementation may support full-site configuration packages only. Future scoped packages may update graphics, spaces/equipment, schedules, or controller applications independently, but every scope must be explicit, previewable and reversible.

# 8. Upload and As-Built Synchronization

Field commissioning may create legitimate differences from the original offline project. Legion therefore needs an upload/retrieve workflow rather than assuming the offline project always remains current.

1.  Connect to and authenticate with the LS-100.

2.  Read active configuration version and a normalized configuration snapshot.

3.  Compare the live snapshot with the local engineering project.

4.  Classify differences as engineering changes, commissioning/as-built changes, runtime-only state or protected live data.

5.  Let the engineer selectively accept as-built configuration changes into a new project revision.

6.  Never import live history, alarms, passwords or transient present values into the offline project.

7.  Build future deployments from the reconciled project revision.

DECIDED  Upload does not mean database backup. Upload retrieves configuration/as-built information into the engineering project; backup remains a separate LS-100 recovery artifact.

# 9. LCPE and Controller Deployment

LCPE owns controller applications. The site package may reference an LPC application by stable application ID, compatible controller model, source revision, built artifact checksum and version.

| Action | Owner | Target |
| --- | --- | --- |
| Create/edit controller logic | LCPE | Offline LPC application project |
| Build/validate application | LCPE | Versioned controller artifact |
| Associate application with equipment | Engineering Workspace | Site project |
| Download application | LCPE directly or authorized mediated workflow | LPC0810/LPCV |
| Record deployed version | LS-100 | Equipment/controller inventory |
| Upload controller configuration | LCPE | Offline controller project/as-built revision |

DECIDED  Deploying a site package to LS-100 does not by itself prove that every physical LPC controller received its application. Controller transfer and verification must have explicit status.

# 10. Development and Transition Strategy

The present legion-web repository combines Engineering and Operator experiences and uses one backend/database. That may remain temporarily, but the architecture must introduce explicit project and live boundaries.

## Development profiles

| Profile | Purpose | Database |
| --- | --- | --- |
| Engineering | Offline project authoring | Engineering project store |
| LS-100 Simulation | Local target that behaves like a commissioned server | Separate live operational database |
| Production LS-100 | Customer runtime | Device-local operational database |

Do not use SEED_DEMO_SITES for customer or reference-project creation.

Development seeds may create users, roles and test fixtures only when explicitly enabled.

Create a repeatable Strip Plaza engineering project fixture/export for development, clearly labeled non-production.

Prove build → export/deploy → stage → validate → activate → rollback using separate local databases before remote deployment.

Preserve existing Operator functionality while the deployment boundary is introduced incrementally.

# 11. Security, Compatibility & Audit

Mutual authentication or equivalent strong identity for Engineering Workspace and LS-100.

Role-based deployment permission separate from ordinary operator control.

Signed packages and checksums verified before staging/activation.

Replay protection and explicit target Site/LS-100 identity.

Compatibility matrix across package schema, LS-100 runtime, Sentry G1 and LPC application versions.

No secrets embedded in exported packages.

Audit entry for build, transfer, validation, activation, failure, rollback and upload.

Configurable approval/annotation requirements for production deployments.

Safe handling and scanning of removable-media imports.

## One-site enforcement

LS-100 rejects activation of a package for a different Site while another Site is active unless an authorized recommissioning workflow first archives and removes the existing Site. Ordinary version upgrades must preserve the same stable Site identity.

# 12. Implementation Acceptance Criteria

Engineering and live configurations use separate storage boundaries.

A validated project builds a deterministic .lspkg.

The package can be exported and imported without a database dump.

Direct deploy and offline import share validation and activation services.

LS-100 allows exactly one active Site.

Activation preserves users, secrets, history, events, audit logs and live runtime state where appropriate.

Every deployment creates a recoverable pre-deployment backup.

Failed activation cannot leave a partially active configuration.

Operator Mode reads only the active LS-100 configuration.

Upload/as-built comparison is distinct from backup/restore.

LCPE controller applications remain separately versioned and explicitly verified.

No production behavior depends on SEED_DEMO_SITES.

## Decision register

| ID | Decision |
| --- | --- |
| DEP-001 | One active Legion Site per LS-100; multiple buildings allowed. |
| DEP-002 | Offline site engineering is owned by the Legion Engineering Workspace. |
| DEP-003 | Deployment artifact is the versioned Legion Site Package (.lspkg). |
| DEP-004 | Direct deploy and offline import use the same package pipeline. |
| DEP-005 | LS-100 stages, validates, backs up, activates and can roll back. |
| DEP-006 | Runtime history, events, users and secrets are not overwritten by normal deployment. |
| DEP-007 | LCPE owns controller applications; site deployment and controller download remain distinct. |
| DEP-008 | Production LS-100 commissioning never depends on development seeds. |

## Industry pattern references

Johnson Controls Metasys SCT transfers an offline archive database to a Site Director/server or engine and supports later uploads; Trane tools similarly save and transfer controller configurations. Legion adopts the durable offline-to-live pattern while using a portable validated package rather than a raw database replacement.

References: https://docs.johnsoncontrols.com/bas/r/Metasys/en-US/SCT-System-Configuration-Tool-Help/14.2/Tools-Menu/Manage-Archive/Download

https://docs.johnsoncontrols.com/bas/r/Metasys/en-US/SCT-Pro-Help/16.0/Working-with-archives/How-do-I-transfer-an-archive-from-SCT-Pro-to-a-server-or-network-engine-download

https://support.trane.com/hc/en-us/articles/30674808265869-Converting-a-UC400-to-Symbio-500